## Calculator
| Buck-Boost Selection Calculator - Rev 3.3 | [12 empty] | Revised Feb 10,2012
password = boost
|  |  |  | 1. Enter the load voltage you need here |  |  |  |  | 208 | Volts
|  |  |  | 2. Enter the load current you need here |  |  |  |  | 20 | Amps
3. Choose the closest voltage combination from the charts below
4. Select catalog number and wiring diagram number.
[24 empty] | amperage for HV as the Load | amperage for HV as the Load | [10 empty] | amperage for LV as the Load
| Single Phase Buck-Boost Selection Calculator | [21 empty] | 1 | 50 | 100 | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 3000 | 5000 | 1 | 50 | 100 | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 3000 | 5000
Voltage |  | L/H | H/L | Low |  | Load = High | High Load Unit | Wiring |  | High |  | Load = Low | Low Load Unit | Wiring |  | xx for LV | xx for HV |  |  |  | Max volt
208 |  | 0.83333 | 1.2 | --- | to | --- | --- | --- | Or | --- | to | --- | --- | --- | 2 | --- | --- | 12 | 120 | 24 | 151.2 |  | 0.041667 | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 | 0.05 | 2.5 | 5 | 7.5 | 12.5 | 25 | 37.5 | 50 | 75 | 100 | 150 | 250
|  | 0.90833 | 1.1009 | --- | to | --- | --- | --- | Or | --- | to | --- | --- | --- | 1 | --- | --- | 11 | 120 | 12 | 138.6 |  | 0.083333 | 4.1667 | 8.3333 | 12.5 | 20.8333 | 41.6667 | 62.5 | 83.3333 | 125 | 166.6667 | 250 | 416.6667 | 0.091667 | 4.5833 | 9.1667 | 13.75 | 22.9167 | 45.8333 | 68.75 | 91.6667 | 137.5 | 183.3333 | 275 | 458.3333
|  | 0.90833 | 1.1009 | 188.9333 | to | 208 | 416-1131-000 | 4 | Or | 228.9908 | to | 208 | 416-1131-000 | 4 | 4 | 31 | 31 | 10 | 240 | 24 | 277.2 |  | 0.041667 | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 | 0.045833 | 2.2917 | 4.5833 | 6.875 | 11.4583 | 22.9167 | 34.375 | 45.8333 | 68.75 | 91.6667 | 137.5 | 229.1667
|  | 0.95238 | 1.05 | 198.0952 | to | 208 | 416-1121-000 | 3 | Or | 218.4 | to | 208 | 416-1121-000 | 3 | 3 | 21 | 21 | 9 | 240 | 12 | 264.6 |  | 0.083333 | 4.1667 | 8.3333 | 12.5 | 20.8333 | 41.6667 | 62.5 | 83.3333 | 125 | 166.6667 | 250 | 416.6667 | 0.0875 | 4.375 | 8.75 | 13.125 | 21.875 | 43.75 | 65.625 | 87.5 | 131.25 | 175 | 262.5 | 437.5
|  | 0.88333 | 1.1321 | --- | to | --- | --- | --- | Or | --- | to | --- | --- | --- | 1 | --- | --- | 8 | 120 | 16 | 142.8 |  |  | 3.125 | 6.25 | 9.375 | 15.625 | 31.25 | 46.875 | 62.5 | 93.75 | 125 | 187.5 | 312.5 |  | 3.5417 | 7.0833 | 10.625 | 17.7083 | 35.4167 | 53.125 | 70.8333 | 106.25 | 141.6667 | 212.5 | 354.1667
|  | 0.78947 | 1.2667 | --- | to | --- | --- | --- | Or | --- | to | --- | --- | --- | 2 | --- | --- | 7 | 120 | 32 | 159.6 |  |  | 1.5625 | 3.125 | 4.6875 | 7.8125 | 15.625 | 23.4375 | 31.25 | 46.875 | 62.5 | 93.75 | 156.25 |  | 1.9792 | 3.9583 | 5.9375 | 9.8958 | 19.7917 | 29.6875 | 39.5833 | 59.375 | 79.1667 | 118.75 | 197.9167
|  | 0.88136 | 1.1346 | 183.322 | to | 208 | 416-1241-000 | 4 | Or | 236 | to | 208 | 416-1241-000 | 4 | 4 | 41 | 41 | 6 | 240 | 32 | 285.6 |  |  | 1.5625 | 3.125 | 4.6875 | 7.8125 | 15.625 | 23.4375 | 31.25 | 46.875 | 62.5 | 93.75 | 156.25 |  | 1.7708 | 3.5417 | 5.3125 | 8.8542 | 17.7083 | 26.5625 | 35.4167 | 53.125 | 70.8333 | 106.25 | 177.0833
|  | 0.9375 | 1.0667 | 195 | to | 208 | 416-1231-000 | 3 | Or | 221.8667 | to | 208 | 416-1231-000 | 3 | 3 | 31 | 31 | 5 | 240 | 16 | 268.8 |  |  | 3.125 | 6.25 | 9.375 | 15.625 | 31.25 | 46.875 | 62.5 | 93.75 | 125 | 187.5 | 312.5 |  | 3.3333 | 6.6667 | 10 | 16.6667 | 33.3333 | 50 | 66.6667 | 100 | 133.3333 | 200 | 333.3333
|  | 0.83333 | 1.2 | 173.3333 | to | 208 | 416-1451-000 | 2 | Or | 249.6 | to | 208 | 416-1451-000 | 2 | 2 | 51 | 51 | 4 | 240 | 48 | 302.4 |  |  | 1.0417 | 2.0833 | 3.125 | 5.2083 | 10.4167 | 15.625 | 20.8333 | 31.25 | 41.6667 | 62.5 | 104.1667 |  | 1.25 | 2.5 | 3.75 | 6.25 | 12.5 | 18.75 | 25 | 37.5 | 50 | 75 | 125
Current |  | 0.91042 | 1.0984 | 189.3667 | to | 208 | 416-1451-000 | 4 | Or | 228.4668 | to | 208 | 416-1451-000 | 4 | 4 | 51 | 51 | 3 | 480 | 48 | 554.4 |  |  | 1.0417 | 2.0833 | 3.125 | 5.2083 | 10.4167 | 15.625 | 20.8333 | 31.25 | 41.6667 | 62.5 | 104.1667 |  | 1.1458 | 2.2917 | 3.4375 | 5.7292 | 11.4583 | 17.1875 | 22.9167 | 34.375 | 45.8333 | 68.75 | 114.5833
20 |  | 0.95208 | 1.0503 | 198.0333 | to | 208 | 416-1431-000 | 3 | Or | 218.4683 | to | 208 | 416-1431-000 | 3 | 3 | 31 | 31 | 2 | 480 | 24 | 529.2 |  |  | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 |  | 2.1875 | 4.375 | 6.5625 | 10.9375 | 21.875 | 32.8125 | 43.75 | 65.625 | 87.5 | 131.25 | 218.75
[22 empty] | +1 | 00 | 01 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | --- | 00 | 01 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | ---
| Three Phase Open Delta Buck-Boost Selection Calculator | [22 empty] | 0 | 1 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 |  | 0 | 1 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91
| Requires two identical Buck-Boost Transformers | [21 empty] | 1 | 50 | 100 | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 3000 | 5000 | 1 | 50 | 100 | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 3000 | 5000
Voltage |  | L/H | H/L | Low |  | Load = High | High Load Unit | Wiring |  | High |  | Load = Low | Low Load Unit | Wiring |  | xx for LV | xx for HV |  |  |  | Max volt
208 |  | 0.95417 | 1.048 | 198.4667 | to | 208 | 416-1121-000 | 11 | Or | 217.9913 | to | 208 | 416-1121-000 | 11 | 11 | 21 | 21 | 9 | 240 | 12 | 264.6 |  | 0.083333 | 4.1667 | 8.3333 | 12.5 | 20.8333 | 41.6667 | 62.5 | 83.3333 | 125 | 166.6667 | 250 | 416.6667 | 0.0875 | 4.375 | 8.75 | 13.125 | 21.875 | 43.75 | 65.625 | 87.5 | 131.25 | 175 | 262.5 | 437.5
|  | 0.90435 | 1.1058 | 188.1043 | to | 208 | 416-1131-000 | 12 | Or | 230 | to | 208 | 416-1131-000 | 12 | 12 | 31 | 31 | 8 | 240 | 24 | 277.2 |  | 0.041667 | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 | 0.045833 | 2.2917 | 4.5833 | 6.875 | 11.4583 | 22.9167 | 34.375 | 45.8333 | 68.75 | 91.6667 | 137.5 | 229.1667
|  | 0.9375 | 1.0667 | 195 | to | 208 | 416-1231-000 | 11 | Or | 221.8667 | to | 208 | 416-1231-000 | 11 | 11 | 31 | 31 | 7 | 240 | 16 | 268.8 |  |  | 3.125 | 6.25 | 9.375 | 15.625 | 31.25 | 46.875 | 62.5 | 93.75 | 125 | 187.5 | 312.5 |  | 3.3333 | 6.6667 | 10 | 16.6667 | 33.3333 | 50 | 66.6667 | 100 | 133.3333 | 200 | 333.3333
|  | 0.88136 | 1.1346 | 183.322 | to | 208 | 416-1241-000 | 12 | Or | 236 | to | 208 | 416-1241-000 | 12 | 12 | 41 | 41 | 6 | 240 | 32 | 285.6 |  |  | 1.5625 | 3.125 | 4.6875 | 7.8125 | 15.625 | 23.4375 | 31.25 | 46.875 | 62.5 | 93.75 | 156.25 |  | 1.7708 | 3.5417 | 5.3125 | 8.8542 | 17.7083 | 26.5625 | 35.4167 | 53.125 | 70.8333 | 106.25 | 177.0833
|  | 0.90909 | 1.1 | 189.0909 | to | 208 | 416-1431-000 | 9 | Or | 228.8 | to | 208 | 416-1431-000 | 9 | 9 | 31 | 31 | 5 | 240 | 24 | 277.2 |  |  | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 |  | 2.2917 | 4.5833 | 6.875 | 11.4583 | 22.9167 | 34.375 | 45.8333 | 68.75 | 91.6667 | 137.5 | 229.1667
|  | 0.83333 | 1.2 | 173.3333 | to | 208 | 416-1451-000 | 10 | Or | 249.6 | to | 208 | 416-1451-000 | 10 | 10 | 51 | 51 | 4 | 240 | 48 | 302.4 |  |  | 1.0417 | 2.0833 | 3.125 | 5.2083 | 10.4167 | 15.625 | 20.8333 | 31.25 | 41.6667 | 62.5 | 104.1667 |  | 1.25 | 2.5 | 3.75 | 6.25 | 12.5 | 18.75 | 25 | 37.5 | 50 | 75 | 125
Enter Desired Current |  | 0.95208 | 1.0503 | 198.0333 | to | 208 | 416-1431-000 | 11 | Or | 218.4683 | to | 208 | 416-1431-000 | 11 | 11 | 31 | 31 | 3 | 480 | 24 | 529.2 |  |  | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 |  | 2.1875 | 4.375 | 6.5625 | 10.9375 | 21.875 | 32.8125 | 43.75 | 65.625 | 87.5 | 131.25 | 218.75
20 |  | 0.91042 | 1.0984 | 189.3667 | to | 208 | 416-1451-000 | 12 | Or | 228.4668 | to | 208 | 416-1451-000 | 12 | 12 | 51 | 51 | 2 | 480 | 48 | 554.4 |  |  | 1.0417 | 2.0833 | 3.125 | 5.2083 | 10.4167 | 15.625 | 20.8333 | 31.25 | 41.6667 | 62.5 | 104.1667 |  | 1.1458 | 2.2917 | 3.4375 | 5.7292 | 11.4583 | 17.1875 | 22.9167 | 34.375 | 45.8333 | 68.75 | 114.5833
[16 empty] | --- | [6 empty] | 00 | 01 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | --- | 00 | 01 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | ---
---
| Three Phase Wye Buck-Boost Selection Calculator | [22 empty] | 0 | 1 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | 00 | 0 | 1 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91
| Requires three identical Buck-Boost Transformers | [21 empty] | 1 | 50 | 100 | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 3000 | 5000 | 1 | 50 | 100 | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 3000 | 5000
Voltage |  | L/H | H/L | Low |  | Load = High | High Load Unit | Wiring |  | High |  | Load = Low | Low Load Unit | Wiring |  | xx for LV | xx for HV |  |  |  | Max volt
208 |  | 0.83173 | 1.2023 | 173 | to | 208 | 416-1131-000 | 6 | Or | 250.0809 | to | 208 | 416-1131-000 | 6 | 6 | 31 | 31 | 11 | 120 | 24 | 261.576 |  | 0.041667 | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 | 0.05 | 2.5 | 5 | 7.5 | 12.5 | 25 | 37.5 | 50 | 75 | 100 | 150 | 250
|  | 0.90865 | 1.1005 | 189 | to | 208 | 416-1121-000 | 5 | Or | 228.9101 | to | 208 | 416-1121-000 | 5 | 5 | 21 | 21 | 10 | 120 | 12 | 239.778 |  | 0.083333 | 4.1667 | 8.3333 | 12.5 | 20.8333 | 41.6667 | 62.5 | 83.3333 | 125 | 166.6667 | 250 | 416.6667 | 0.091667 | 4.5833 | 9.1667 | 13.75 | 22.9167 | 45.8333 | 68.75 | 91.6667 | 137.5 | 183.3333 | 275 | 458.3333
|  | 0.90865 | 1.1005 | 189 | to | 208 | 416-1131-000 | 8 | Or | 228.9101 | to | 208 | 416-1131-000 | 8 | 8 | 31 | 31 | 9 | 240 | 24 | 479.556 |  | 0.041667 | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 | 0.045833 | 2.2917 | 4.5833 | 6.875 | 11.4583 | 22.9167 | 34.375 | 45.8333 | 68.75 | 91.6667 | 137.5 | 229.1667
|  | 0.95195 | 1.0505 | 198.0046 | to | 208 | 416-1121-000 | 7 | Or | 218.5 | to | 208 | 416-1121-000 | 7 | 7 | 21 | 21 | 8 | 240 | 12 | 457.758 |  | 0.083333 | 4.1667 | 8.3333 | 12.5 | 20.8333 | 41.6667 | 62.5 | 83.3333 | 125 | 166.6667 | 250 | 416.6667 | 0.0875 | 4.375 | 8.75 | 13.125 | 21.875 | 43.75 | 65.625 | 87.5 | 131.25 | 175 | 262.5 | 437.5
|  | 0.78846 | 1.2683 | 164 | to | 208 | 416-1241-000 | 6 | Or | 263.8049 | to | 208 | 416-1241-000 | 6 | 6 | 41 | 41 | 7 | 120 | 32 | 276.108 |  |  | 1.5625 | 3.125 | 4.6875 | 7.8125 | 15.625 | 23.4375 | 31.25 | 46.875 | 62.5 | 93.75 | 156.25 |  | 1.9792 | 3.9583 | 5.9375 | 9.8958 | 19.7917 | 29.6875 | 39.5833 | 59.375 | 79.1667 | 118.75 | 197.9167
|  | 0.87981 | 1.1366 | 183 | to | 208 | 416-1231-000 | 5 | Or | 236.4153 | to | 208 | 416-1231-000 | 5 | 5 | 31 | 31 | 6 | 120 | 16 | 247.044 |  |  | 3.125 | 6.25 | 9.375 | 15.625 | 31.25 | 46.875 | 62.5 | 93.75 | 125 | 187.5 | 312.5 |  | 3.5417 | 7.0833 | 10.625 | 17.7083 | 35.4167 | 53.125 | 70.8333 | 106.25 | 141.6667 | 212.5 | 354.1667
|  | 0.88221 | 1.1335 | 183.5 | to | 208 | 416-1241-000 | 8 | Or | 235.7711 | to | 208 | 416-1241-000 | 8 | 8 | 41 | 41 | 5 | 240 | 32 | 494.088 |  |  | 1.5625 | 3.125 | 4.6875 | 7.8125 | 15.625 | 23.4375 | 31.25 | 46.875 | 62.5 | 93.75 | 156.25 |  | 1.7708 | 3.5417 | 5.3125 | 8.8542 | 17.7083 | 26.5625 | 35.4167 | 53.125 | 70.8333 | 106.25 | 177.0833
|  | 0.9375 | 1.0667 | 195 | to | 208 | 416-1231-000 | 7 | Or | 221.8667 | to | 208 | 416-1231-000 | 7 | 7 | 31 | 31 | 4 | 240 | 16 | 465.024 |  |  | 3.125 | 6.25 | 9.375 | 15.625 | 31.25 | 46.875 | 62.5 | 93.75 | 125 | 187.5 | 312.5 |  | 3.3333 | 6.6667 | 10 | 16.6667 | 33.3333 | 50 | 66.6667 | 100 | 133.3333 | 200 | 333.3333
Enter Desired Current |  | 0.90868 | 1.1005 | 189.0046 | to | 208 | 416-1431-000 | 5 | Or | 228.9045 | to | 208 | 416-1431-000 | 5 | 5 | 31 | 31 | 3 | 240 | 24 | 479.556 |  |  | 2.0833 | 4.1667 | 6.25 | 10.4167 | 20.8333 | 31.25 | 41.6667 | 62.5 | 83.3333 | 125 | 208.3333 |  | 2.2917 | 4.5833 | 6.875 | 11.4583 | 22.9167 | 34.375 | 45.8333 | 68.75 | 91.6667 | 137.5 | 229.1667
20 |  | 0.83173 | 1.2023 | 173 | to | 208 | 416-1451-000 | 6 | Or | 250.0809 | to | 208 | 416-1451-000 | 6 | 6 | 51 | 51 | 2 | 240 | 48 | 523.152 |  |  | 1.0417 | 2.0833 | 3.125 | 5.2083 | 10.4167 | 15.625 | 20.8333 | 31.25 | 41.6667 | 62.5 | 104.1667 |  | 1.25 | 2.5 | 3.75 | 6.25 | 12.5 | 18.75 | 25 | 37.5 | 50 | 75 | 125
[23 empty] | 00 | 01 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | --- | 00 | 01 | 11 | 21 | 31 | 41 | 51 | 61 | 71 | 81 | 91 | ---

## Wiring
1
2
3
4
5
6
7
8
9
10
11
12